## Slide 1: Slide Title for Accessibility 01
June 23, 2025
Huzaifah Nadeem and Dr. Amy Babay
Using Digital Twins as an Upgrade Path for Critical Infrastructure Control Systems
Workshop on Digital Twins for Dependability, Resilience and Security (DT4DRS) at DSN 2025

## Slide 2: Slide Title for Accessibility 09
Supervisory Control and Data Acquisition (SCADA) systems
SCADA systems control and operate power grid infrastructure
  Critical to other systems
Servers, known as SCADA Masters (SMs), process clients’ updates and commands
Clients
  Human Machine Interfaces (HMI)
  Remote Terminal Units (RTU)
  Programmable Logic Controllers (PLC)
Remote Physical Equipment (Substation)
PLCs/RTUs
Network
Control Center
SMs
HMIs
SCADA

## Slide 3: Slide Title for Accessibility 09
Resilience in SCADA systems
…
HMI
PLCs, other devices
SCADA IT DT
Primary + Backup SCADA Servers
Intrusion-Tolerant Digital Twins offer a path to transition
Modern Industrial SCADA
…
HMI
PLCs, other devices
Primary SCADA Server
Backup SCADA Server
Today’s systems are vulnerable to cyberattacks
Intrusion-Tolerant SCADA
…
HMI
PLCs, other devices
Replicated, Diverse SCADA Servers
We know how to build more resilient systems
Out-of-band output comparison
Out-of-band output comparison supports intrusion detection in the near term
“Network-Attack-Resilient Intrusion-Tolerant SCADA for the Power Grid”
A. Babay, T. Tantillo, T. Aron, M. Platania, and Y. Amir, IEEE DSN, 2018
Intrusion-Tolerant Digital Twins will enable us to transition today’s vulnerable SCADA systems to intrusion tolerant architectures
“On the Challenges of Building a BFT SCADA”
A. Nogueira, M. Garcia, A. Bessani, and N. Neves, IEEE DSN, 2018
Notes: mention Byzantine Fault Tolerance and consensus

## Slide 4: Slide Title for Accessibility 09
Upgrades for Emerging Threats
Modern Industrial SCADA
…
HMI
PLCs, other devices
Primary SCADA Server
Backup SCADA Server
Intrusion-Tolerant SCADA
…
HMI
PLCs, other devices
Replicated, Diverse SCADA Servers
Upgraded Intrusion-Tolerant SCADA
…
HMI
PLCs, other devices
Intrusion-tolerant DT deployment
Upgraded Intrusion-tolerant DT deployment
?
Intrusion-Tolerant Digital Twins will enable easily upgrading architectures to address new threats
“Tolerating Compound Threats in Critical Infrastructure Control Systems”
S. Bommareddy, M. Khan, H. Nadeem, B. Gilby, I. Chiu, J. W. van de Lindt, O. Nofal, M. Panteli, L. Wells II, Y. Amir, and A. Babay, SRDS 2024

## Slide 5: Slide Title for Accessibility 09
Design Considerations
The system should not have to go offline for each upgrade
Protocol differences should not limit us with component upgrades
We should be able to seamlessly transfer control from one instance to another
  Should not require a lot of set up
  Trusted administrator
Ability to compare system instances’ logs
  To verify that all instances are behaving the same way
  Helps build confidence before we actually transfer control to one particular instance
Notes: - new components can have different protocols and might not work with existing stuff like you dont have to update your HMI etc when you are updating replicas
- being able to seamlessly transfer control. how do you initiate a control transfer? you need a trusted administrator. easily initiate this without a lot of set up
- being able to compare system logs and tell if they are doing the same thing before we actually commit to using one particular system instance

## Slide 6: Slide Title for Accessibility 09
Spire – an Intrusion-Tolerant SCADA system
Clients: HMI, RTUs, and PLCs
Proxies:
  Translate DNP3 and Modbus protocols used by RTUs and PLCs for the rest of the system
  Verifies signatures of the messages going to its clients and sign messages going out to the SMs.
Replicas:
  SM for application logic
  Prime Daemons for consensus protocol logic
Overlay networks using Spines
“Practical Intrusion-Tolerant Networks”
D. Obenshain, T. Tantillo, A. Babay, J. Schultz, A. Newell, M. Hoque, Y. Amir, and C. Nita-Rotaru
ICDCS 2016
“Prime: Byzantine Replication Under Attack”
Y. Amir, B. Coan, J. Kirsch, J. Lane
IEEE Transactions on Dependable and Secure Computing 2011

## Slide 7: Slide Title for Accessibility 09
Design and Technique Overview
Main idea: have parallel live-running digital twin instance of our system
  One active instance with a number of twin instances
The instances can differ in terms of the configurations they use, code-level diversity, and even the communication protocols they use.
We used Spire as our base
Modifications and additions to Spire
  Proxies
  Data Collector
  Switcher
  Management Network for communication between these new components
new
modified

## Slide 8: Slide Title for Accessibility 09
Proxies
Proxies mirror messages between the clients and the system instances
Internally, each instance has a corresponding process for communication (I/O Process)
I/O processes also allow us to easily add and remove instances from the system by forking new processes or killing existing processes without the proxy needing to go offline
These processes can manage any necessary translation that may be required for communication with an instance
Proxy
Instance 1
Instance 2
Instance k
Clients
I/O Process k
I/O Process 2
I/O Process 1
…
…
Notes: emphasize the point about translation

## Slide 9: Slide Title for Accessibility 09
Data Collector
Data Collector stores all of the instances’ logs
It receives all the messages that the proxies receive and forward
Here an intrusion detection algorithm can run that compares the different instances logs to detect anomalies
The logs are also useful for the operator to analyze and build confidence on using a particular configuration
Proxy 1
Data Collector
Proxy 2
Proxy n
…
Management Network
Updates and Commands from the instances and clients
Forwards copies of the messages

## Slide 10: Slide Title for Accessibility 09
Switcher
The operator can seamlessly transfer control between the instances by using the Switcher.
After entering the relevant command into the Switcher, it sends a message to the proxies via the management network
  The proxies then handle the updates to the data structures to forward messages to the right places and handle addition/removal of the relevant I/O Processes
Switcher only needs to be online when the operator wants to send a message
Switcher
Operator enters a command
Management Network
Multicast
Proxy 1
Proxy 2
Proxy n
…
Proxies update the data structures and add/remove I/O Processes as necessary
Data Collector

## Slide 11: Slide Title for Accessibility 09
Management Network
The management network connects these new components
The management network can be a separate physical network, or a logical overlay network on top of the existing physical network
For our prototype, we use Spines to deploy the management network as an overlay
Management Network
Proxy 1
Proxy 2
Proxy n
…
Data Collector
Switcher

## Slide 12: Slide Title for Accessibility 09
A Challenge: State Divergence Between the Instances
Since the proxies send messages to the system instances over a network, delays and reordering of messages is possible
That can result in application’s state divergence between the instances
The divergence can also be non-benign in nature, such as if an attacker introduces new commands
  It is useful to detect that for intrusion detection
Proxy
Instance 1
Instance 2
Network can reorder and delay messages
m1
m2
m3
m4
m1
m2
m3
m4
< m1 ,m2, m3, m4>
< m1 , _, m3, m4, m2>

## Slide 13: Slide Title for Accessibility 09
A Challenge: State Divergence Between the Instances (cont’d)
We want
  to be able to transfer control to a new system instance. For this to work correctly, its state should match that of the previous active instance.
  to be able to compare outputs between instances for intrusion detection. However, if outputs can differ for benign reasons, how do we detect problematic/malicious divergence?
For our prototype with Spire, the ground truth is the state at the clients
Therefore, the SMs only update their data structures upon receiving updates from the PLCs/RTUs
  This will help us with (1)

## Slide 14: Slide Title for Accessibility 09
A Challenge: State Divergence Between the Instances (cont’d)
For (2) i.e., distinguishing between benign and malicious divergence:
  If an attacker introduces completely new commands that the other instances’ states do not have, that is detectable by comparing to the other states
  However, the attacker can reorder commands
  For our specific application, the operator can see the state and if some condition needs to met, that can be verified first before initiating the next command
This is one way of addressing the state divergence issue i.e., have application-specific state divergence solution
However, there may be more general solutions

## Slide 15: Slide Title for Accessibility 09
Future Directions
Exploration of other solutions regarding our application state divergence
Developing more advanced intrusion detection techniques applied live on the instances’ logs at the data collector
Exploring the possibilities to extend intrusion-tolerant Cyber Digital Twins to the client level (i.e., RTUs, PLCs, HMIs.)
Conducting a real-world case study where we use this technique and approach as an upgrade path for a deployed system
Increasing the scope and the ideas applied to other control systems or Cyber-Physical systems more broadly.
Notes: We are already working on point 4 about doing it on a real SCADA system. can mention energy innovation center.

## Slide 16: Slide Title for Accessibility 09
Conclusion
We developed an approach on using digital twins to make system upgrades easier and more manageable.
This approach will help, now and in the future, with upgrading the systems without making the systems go offline.
Other benefits include intrusion detection by comparing system instances’ logs
For this, we developed a prototype on a real SCADA system Spire
We also described the issues and challenges we encountered and some possible ways to address them.
Notes: Emphasize point #2

## Slide 17: Slide Title for Accessibility 21
h.nadeem@pitt.edu
Questions?